EUROTHERM

DRIVES

|  | 506/507/508 |
| --- | --- |

|  | Product Manual |
| --- | --- |
|  | HA389427 Issue 7 |

Ó Copyright Eurotherm Drives Limited 2026

All rights strictly reserved. No part of this document may be stored in a retrieval system, or transmitted in any form or by any means to persons not employed by a Eurotherm group company without written permission from Eurotherm Drives Ltd.

Although every effort has been taken to ensure the accuracy of this document it may be necessary, without notice, to make amendments or correct omissions. Eurotherm Drives cannot accept responsibility for damage, injury, or expenses resulting therefrom.

WARRANTY Eurotherm Drives warrants the goods against defects in design, materials and workmanship for the period of 12 months from the date of delivery on the terms detailed in Eurotherm Drives Standard Conditions of Sale IA058393C. Eurotherm Drives reserves the right to change the content and product specification without notice.

Requirements

- Please read this information BEFORE installing the equipment.

#### Intended Users

This manual is to be made available to all persons who are required to install, configure or service equipment described herein, or any other associated operation.

The information given is intended to highlight safety issues, and to enable the user to obtain maximum benefit from the equipment.

Complete the following table for future reference detailing how the unit is to be installed and used.

| INSTALLATION DETAILS |  |
| --- | --- |
| Serial Number (see product label) |  |
| Where installed (for your own information) |  |
| Unit used as a: (refer to Certification for the 506/507/508) | o Component o Relevant Apparatus |
| Unit fitted: | o Wall-mounted o Enclosure |

#### Application Area

The equipment described is intended for industrial motor speed control.

#### Personnel

Installation, operation and maintenance of the equipment should be carried out by qualified personnel. A qualified person is someone who is technically competent and familiar with all safety information and established safety practices; with the installation process, operation and maintenance of this equipment; and with all the hazards involved.

Hazards

- This equipment can endanger life through rotating machinery and high voltages. Failure to observe the following will constitute an ELECTRICAL SHOCK HAZARD.   These controllers are non-isolated products, both control and power circuitry are at mains potential.  External control equipment should be used which provides adequate protection for the user against electric shock hazard.

- The equipment must be permanently earthed due to the high earth leakage current.

- Before working on the equipment or filter ensure isolation of the mains supply from terminals L1 and L2.

- The drive motor must be connected to an appropriate safety earth.

- The EMC filter equipment contains high value capacitors which take time to discharge after removal of the mains supply.  Wait for at least 3 minutes before working on the filter.

- Never perform high voltage resistance checks on the wiring without first disconnecting the drive from the circuit being tested.

- When replacing a drive in an application and before returning to use, it is essential that all user defined parameters for the product’s operation are correctly installed.

- This equipment contains electrostatic discharge (ESD) sensitive parts.  Observe static control precautions when handling, installing and servicing this product.

- Metal parts may reach a temperature of 90 degrees centigrade in operation.

#### Application Risk

The specifications, processes and circuitry described herein are for guidance only and may need to be adapted to the user’s specific application.

Eurotherm Drives does not guarantee the suitability of the equipment described in this Manual for individual applications.

Risk Assessment

Under fault conditions, power loss or other operating conditions not intended, the equipment may not operate as specified. In particular:

- The motor speed may not be controlled

- The direction of rotation of the motor may not be controlled

- The motor may be energised

#### Guards

The user must provide guarding and /or additional safety systems to prevent risk of injury and electric shock.

- Thermal sensors contained within the motor must be double insulated.

- All exposed metalwork in the units are protected by basic insulation and bonding to a safety earth.

#### RCDs

These are not recommended for use with this product but, where their use is mandatory, only Type B RCDs should be used.

#### Signal and Control Terminals

This is a non isolated product.  The signal plus control connections are not isolated from the AC supply.

Filter

- AC Supply filters produce earth (ground leakage currents in excess of 3.5mA).

- AC Supply filters contain capacitors, allow at least 1 minute before servicing.

- AC Supply filters should be permanently earthed (grounded), use the second Protective Ground terminal as an independent earth (ground).

- Eurotherm Drives do not recommend the use of RCDs.  Special RCDs (type B-IEC755) are required due to AC and DC components flowing in the earth (ground) leakage current.  All loads requiring protection with an RCD would be at risk.

Chapter 1	Product Overview

Description	1-1

Product Range	1-1

Chapter 2	Overview of the 506/507/508

- User Supplied Primary Components	2-2

- Optional Ancillary Components	2-2

Chapter 3	Terminal Description

Power Terminals	3-2

Auxiliary Terminals	3-2

Switches	3-3

Potentiometers	3-3

LEDS	3-3

Chapter 4	Installing the 506/507/508

Installation	4-1

Speed Control	4-1

Current Control	4-1

Wire Sizes	4-2

Requirements for UL Compliance	4-3

Motor Overload Protection	4-3

Short Circuit Protection Requirements	4-3

Short Circuit Rating	4-3

Operating Ambient Temperature	4-3

Field Wiring Temperature Rating	4-3

Field Wiring Terminal Markings	4-3

Power Wiring Terminals	4-3

Terminal Tightening Torque	4-4

Field Grounding Terminals	4-4

Fitting	4-5

Block Diagram	4-6

Filter	4-8

EMC Connections	4-9

Installation and Set-Up	4-9

Warning	4-9

- Switch Selection	4-9

- Potentiometer	4-10

- Motor	4-10

- Wiring	4-10

Applying Power	4-10

Fault Finding	4-12

Chapter 5	Routine Maintenance and Repair

Routine Maintenance	5-1

Repair	5-1

Returning the Unit to Eurotherm Drives	5-1

Chapter 6	Certification for the 506/507/508

EC Declaration of Conformity (EMC Directive)	6-2

Manufacturer’s EMC Declaration	6-3

EC Declaration of Conformity (Low Voltage Directive)	6-4

Manufacturer’s Declaration	6-5

Chapter 7	Technical Specification

Input  Supply	7-1

Speed Control	7-1

Current (Torque) Control	7-1

Adjustment Range	7-2

Environmental Requirements	7-2

EMC Technical Ratings	7-3

- Immunity	7-3

- Emissions	7-3

Electrical  Ratings	7-4

Output Ratings with typical armature voltage, Va, 80/90V (160/180V)	7-4

Adjustment Ranges	7-4

Product Code	7-5