# Chapter 2	Technical Details

## Electrical Specifications

|  | 5831 |  |  |  |  | N/A |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PARAMETER | 582 |  |  | 583 |  |  | UNITS |
|  | 0.37kW | 0.55kW | 0.75kW | 1.1kW | 1.5kW | 2.2kW |  |
| INPUT RATINGS |  |  |  |  |  |  |  |
| Supply Voltage 1 or 3-phase | 220/240 ± 10% | 220/240 ± 10% | 220/240 ± 10% | 220/240 ± 10% | 220/240 ± 10% | 220/240 ± 10% | Volts AC |
| Max Supply Current 1 ph 3 ph | 4 | 6 3.5 | 8 5 | 10 6 | 15 9 | 20 12 | Amps AC (RMS) |
| Fuse Assembly 1ph | LA058085U014 | LA058085U014 | LA058085U014 | LA058085U024 | LA058085U024 | LA058085U024 |  |
| Fuse Assembly 3ph |  |  | LA058085U014 | LA058085U014 | LA058085U014 | LA058085U024 | 1 per phase |
| Fuse Replacement 1ph | CH430014 10A | CH430014 10A | CH430014 10A | CH430024 20A | CH430024 20A | CH430024 20A |  |
| Fuse Replacement 3ph |  |  | CH430014 10A | CH430014 10A | CH430014 10A | CH430024 20A | 1 per phase |
| Supply Frequency | 50/60 | 50/60 | 50/60 | 50/60 | 50/60 | 50/60 | Hz |
| Power Factor (lag) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 |  |
| OUTPUT RATINGS |  |  |  |  |  |  |  |
| Output Ratings | 220/240 | 220/240 | 220/240 | 220/240 | 220/240 | 220/240 | Volts AC |
| Max Output Current | 2.2 | 3.0 | 4.0 | 5.5 | 7.0 | 10.0 | Amps AC |
| Output Frequency | 0-100/120 | 0-100/120 | 0-100/120 | 0-100/120 | 0-100/120 | 0-100/120 | Hz |
| Heat Dissipation | 25 | 40 | 50 | 65 | 100 | 130 | Watts |
| Output Power | 0.37 | 0.55 | 0.75 | 1.1 | 1.5 | 2.2 | kW |
| Overload | 150 30s | 150 30s | 150 30s | 150 30s | 150 30s | 150 30s | % |

## ENVIRONMENTAL

| HUMIDITY | : | 85% R.H. at 40°C (non condensing). |
| --- | --- | --- |
| ALTITUDE | : | Above 1000m Derate 1%/100m. |
| ATMOSPHERE | : | Non- flammable, non-corrosive and dust free. |
| OPERATING TEMPERATURE | : | 0 to 40°C (Derate 1.5%/Degree above 40°C up to 55°C). |
| 582/583 ENCLOSURE | : | Chassis Mounted either IP00 or IP20. |
| 5831 ENCLOSURE | : | Panel Mounted IP54. |

| ## MECHANICAL |  | Width(mm) | Height(mm) | Depth(mm) | Weight(kg) |  |
| --- | --- | --- | --- | --- | --- | --- |
| 582 IP00 | : | 163 | 237 | 84 | 1.0(1.2) |  |
| 582 IP20 | : | 170 | 247 | 97 | 1.9(2.1) |  |
| 582 IP20 with Gland Plate | : | 170 | 280 | 97 | 2.1(2.3) |  |
| 582 IP20 with Op Station | : | 170 | 247 | 117 | 1.9(2.1) |  |
| 582 IP20 with GP and OS | : | 170 | 280 | 117 | 2.1(2.3) |  |
| 583 IP00 | : | 272 | 250 | 156 | 4.6 |  |
| 583 IP20 | : | 272 | 250 | 165 | 5.2 |  |
| 583 IP20 with Op Station | : | 272 | 250 | 185 | 5.3 |  |
| 5831 IP54 | : | 188 | 255 | 150 | 5.5 |  |
|  |  | Weights in brackets refer to 0.75kW version |  |  |  |  |
| MOUNTING ORIENTATION | : | Vertical |  |  |  |  |
| AIR FLOW CLEARANCE | : | 70mm |  |  |  |  |
| POWER TERMINATIONS | : | Screw Connectors for 2.5mm wire 5822 or 4mm2 583/5831. |  |  |  |  |
| 582 COVER REMOVAL: | : | Press small blunt instrument (e.g. screwdriver) into slot in side of cover and pull gently - see HG057848 for slot location. |  |  |  |  |
| 583 COVER REMOVAL | : | Apply sensible pressure to left-hand side of cover until it comes free from lip of side plate. See drawing HG058065F. |  |  |  |  |
| 5831 COVER REMOVAL | : | Four screws are provided at the corners of the cover when removed the cover can be lifted to allow access to the earth connection. |  |  |  |  |
| TERMINAL PLATE REMOVAL 582/583 | : | Rotate either the single screw in the centre of the 583 plate, or the two side screws on the 582 to remove and gain access to the terminals and user adjustments. |  |  |  |  |
| GLAND PLATE ACCESS HOLES 582 ONLY | : | On the 582 a gland plate (LA057730) can be fixed to the mounting plate to accept 3 x 0.5” NPT conduit connectors, or, using adaptor ring BH058121 in each position, 3 x M20 conduit connectors. If a gland plate is used the old terminal plate should be discarded and the new one provided in the kit used. |  |  |  |  |
| GLAND PLATE ACCESS 5831 | : | On the 5831 a gland plate is provided as a force fit into base. |  |  |  |  |