|  | 584SV Series Frequency Inverter- HA463660 |  |
| --- | --- | --- |
|  | Chapter | 8 |
|  | Routine Maintenance and Repair |  |
|  | Contents Page |  |

- Routine Maintenance

- Spares Information

- Electro-Mechanical Parts

- Printed Circuit Boards

- Repair Procedures

- Printed Circuit Board (PCB) Replacement

- Power Control PCB (AH389167), Calibration Card (AH389444) and Control PCB (AH464162) Replacement

- Switch Mode Power Supply PCB (AH389166) Replacement

- Line Suppression PCB (AH389192) Replacement

- Fan Replacement

- Inverter Main Cooling Fan and Fan Start Capacitor Replacement  (Type 8 & 9)

- Inverter Main Cooling Fan, Internal Extractor Fan and Main Fan Start Capacitor Replacement (Type 10)

- Phase Assembly Replacement

- Phase Assembly Removal Procedure

- Phase Assembly Installation Procedure

# Routine Maintenance and Repair

## Routine Maintenance

Periodically inspect the Inverter for build-up of dust or obstructions that may affect ventilation of the unit. Remove this using dry air.

### Spares Information

Eurotherm Drives are able to provide guidance regarding the necessary component part to be replaced.

#### Electro-Mechanical Parts

The following items are product/kW rating dependant.

| Product Code (Block 2) | Main Cooling Fan |  | Motor Start Capacitor for Main Cooling Fan |  | Internal Extractor Fan (2 required - Type 10 only) |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Fan Voltage |  | Fan Voltage |  | Fan Voltage |  |
|  | 115V | 230V | 115V | 230V | 115V | 230V |
| 0900 (Type 8) | DL389775 | DL464085 | CY389841 | CY464087 | - | - |
| 1100 (Type 8) | DL389775 | DL464085 | CY389841 | CY464087 | - | - |
| 1320 (Type 8) | DL389775 | DL464085 | CY389841 | CY464087 | - | - |
| 1600 (Type 9) | DL389776 | DL464086 | CY389842 | CY464088 | - | - |
| 1800 (Type 9) | DL389776 | DL464086 | CY389842 | CY464088 | - | - |
| 2000 (Type 9) | DL389776 | DL464086 | CY389842 | CY464088 | - | - |
| 2500 (Type 10) | DL389776 | DL464086 | CY389842 | CY464088 | DL049612 | DL049612* |
| 2800 (Type 10) | DL389776 | DL464086 | CY389842 | CY464088 | DL049612 | DL049612* |

* 2 fans wired in series for 230V rating

| Product Code (Block 2) | Phase Assembly | Brake Unit Assembly |
| --- | --- | --- |
| 0900 (Type 8) | LA464082U001 | LA464083U001 |
| 1100 (Type 8) | LA464082U001 | LA464083U001 |
| 1320 (Type 8) | LA464082U001 | LA464083U001 |
| 1600 (Type 9) | LA464082U002 | LA464083U002 |
| 1800 (Type 9) | LA464082U002 | LA464083U002 |
| 2000 (Type 9) | LA464082U002 | LA464083U002 |
| 2500 (Type 10) | LA464082U003 | LA464083U003 |
| 2800 (Type 10) | LA464082U003 | LA464083U003 |

#### Printed Circuit Boards

The printed circuit boards listed below are common to the 584SV Type 8, 9 and 10 series of Inverters.

| PCB Description | Part Number |
| --- | --- |
| Power Control PCB | AH389167U001 |
| Calibration Card PCB | AH389444 (see note below) |
| Control PCB | AH464162U001 |
| Switch Mode Power Supply PCB | AH389166U001 |
| Line Suppression PCB | AH389192U001 |

- If ordering the Calibration Card PCB, please state the power-build of the Inverter.

## Repair Procedures

The 584SV Types 8, 9 and 10 series of Inverters have been designed to be serviceable units. In the unlikely event of component failure, it is possible to replace the faulty item without having to replace the complete drive unit.

Replacement of components should only be carried out by electrically competent personnel with the knowledge/expertise required to perform the relevant operation, i.e. in order to replace component parts, drive disassembly, rebuild and re-testing is required.

Having identified the faulty component, follow the replacement procedure carefully.

- FAILURE TO FOLLOW PROCEDURE MAY RESULT IN DAMAGE TO THE INVERTER AND POSSIBLE ELECTRICAL SHOCK HAZARD! PERSONNEL PERFORMING COMPONENT REPLACEMENT PROCEDURES MUST BE ELECTRICALLY COMPETENT AND POSSESS THE KNOWLEDGE /EXPERTISE REQUIRED TO PERFORM THE RELEVANT OPERATION.

- BEFORE PERFORMING MAINTENANCE ON THIS UNIT, ENSURE ISOLATION OF THE MAIN SUPPLY TO TERMINALS L1, L2 AND L3.

WAIT FOR AT LEAST 5 MINUTES FOR THE DC LINK TERMINALS (DC+ AND DC-) TO DISCHARGE TO SAFE VOLTAGE LEVELS (<50V),
FAILURE TO DO SO CONSTITUTES AN ELECTRICAL SHOCK HAZARD.

This equipment contains electrostatic discharge (ESD) sensitive parts.  Observe static control precautions when handling, installing and servicing this product.

Figure 8-1  Simplified View showing Panels Removed

Figure 8-2  Internal Detail Drawing of the Inverter (typical)

### Printed Circuit Board (PCB) Replacement

- Observe all electrical warnings and static handling precautions.

#### Power Control PCB (AH389167), Calibration Card (AH389444) and Control PCB (AH464162) Replacement

- Undo the two, quarter-turn fasteners on the top of the Inverter casing and remove the front top cover (plastic). Repeat the operation on the bottom terminal cover.

- Disconnect the Operator Station 4-way cable from the P3 port on the Control PCB.

- Undo the four, quarter-turn fasteners to remove the Inverter’s front cover (metal). Take care not to damage PCBs beneath the cover when removing it.

- You will now see the Power Control PCB, Control PCB and Calibration Card mounted on the front of the hinged panel as shown below.

Figure 8-3  View of Power Control PCB, Control PCB and Calibration Card

- Before replacing the PCB take note of how it is connected, ensuring that the new PCB is re-connected correctly.

- Replace the Inverter’s front cover (metal) which is attached using the four, quarter-turn fasteners (take care not to damage PCBs beneath the cover).

- Re-connect the Operator Station  4-way cable to the P3 port on the Control PCB.

- Re-fit the Inverter’s top cover (plastic) using the two quarter-turn fasteners.

- Re-fit the Inverter’s bottom terminal cover (plastic) using the two quarter-turn fasteners.

#### Switch Mode Power Supply PCB (AH389166) Replacement

- Undo the two, quarter-turn fasteners on the top of the Inverter casing and remove the front top cover (plastic). Repeat the operation on the bottom terminal cover.

- Disconnect the Operator Station 4-way cable from the P3 port on the Control PCB.

- Undo the four, quarter-turn fasteners to remove the Inverter’s front cover (metal). Take care not to damage PCBs beneath the cover when removing it.

- Release the hinged panel using the quarter-turn fastener.

- The SMPS PCB will be seen on the back of the hinged panel as shown below.

Figure 8-4  SMPS PCB mounted on the back of the hinged panel

- Before replacing the PCB take note of how it is connected, ensuring that PCB is re-connected correctly.

- Refit the hinged panel, securing in place with the quarter-turn fastener.

- Replace the Inverter’s front cover (metal) which is attached using the four, quarter-turn fasteners (take care not to damage PCBs beneath the cover).

- Re-connect the Operator Station 4-way cable to the P3 port on the Control PCB.

- Re-fit the Inverter’s top cover (plastic) using the two quarter-turn fasteners.

- Re-fit the Inverter’s bottom terminal cover (plastic) using the two quarter-turn fasteners.

#### Line Suppression PCB (AH389192) Replacement

- Undo the two, quarter-turn fasteners on the top of the Inverter casing and remove the front top cover (plastic). Repeat the operation on the bottom terminal cover.

- Disconnect the Operator Station 4-way cable from the P3 port on theControl PCB.

- Undo the four, quarter-turn fasteners to remove the Inverter’s front cover (metal). Take care not to damage PCBs beneath the cover when removing it.

- Release the hinged panel using the quarter-turn fastener.

- You will now see the Line Suppression PCB inside the Inverter as shown below.

- Figure 8-5  Line Suppression PCB

- Before replacing the PCB take note of how it is connected, ensuring that PCB is re-connected correctly.

- Refit the hinged panel, securing in place with the quarter-turn fastener.

- Replace the Inverter’s front cover (metal) which is attached using the four, quarter-turn fasteners (take care not to damage PCBs beneath the cover).

- Re-connect the Operator Station 4-way cable to the P3 port on the Control PCB.

- Re-fit the Inverter’s top cover (plastic) using the two quarter-turn fasteners.

- Re-fit the Inverter’s bottom terminal cover (plastic) using the two quarter-turn fasteners.

### Fan Replacement

- Observe all electrical warnings and static handling precautions.

- When the fan is replaced, ensure that the original wiring loom routing/fixing is preserved. This is an electrical safety requirement.

#### Inverter Main Cooling Fan and Fan Start Capacitor Replacement  (Type 8 & 9)

- Undo the two, quarter-turn fasteners on the top of the Inverter casing and remove the front top cover (plastic). Repeat the operation on the bottom terminal cover.

- Disconnect the Operator Station 4-way cable from the P3 port on the Control PCB.

- Undo the four, quarter-turn fasteners to remove the Inverter’s front cover (metal). Take care not to damage PCBs beneath the cover when removing it.

- Remove the main fan housing.

- Release the hinged panel using the quarter-turn fastener.

- Take note of the fan and fan start capacitor wiring. Disconnect the fan and fan start capacitor wiring.

- Remove the fan mounting and fan start capacitor mounting nuts (it may be easier to remove the capacitor mounted on its bracket, where fitted). Remove the fan and fan start capacitor, taking care not to damage other components within the Inverter.

- Replace the fan and fan start capacitor taking care not to damage other components within the Inverter. Tighten the mounting nuts.

- Re-connect fan wiring loom and ensure that electrical safety isolation is preserved, refer to wiring diagram HJ 463151 D 001, Figure 8-6, page 8-11.

- Re-fit the fan housing.

- Refit the hinged panel, securing in place with the quarter-turn fastener.

- Replace the Inverter’s front cover (metal) which is attached using the four, quarter-turn fasteners (take care not to damage PCBs beneath the cover).

- Re-connect the Operator Station 4-way cable to the P3 port on the Control PCB.

- Re-fit the Inverter’s top cover (plastic) using the two quarter-turn fasteners.

- Re-fit the Inverter’s bottom terminal cover (plastic) using the two quarter-turn fasteners.

#### Inverter Main Cooling Fan, Internal Extractor Fan and Main Fan Start Capacitor Replacement (Type 10)

In addition to the main cooling fan, the Type 10 Inverter also has two internal 120mm square fans. The main cooling fan, internal extractor fans and main fan start capacitor are mounted on the bottom panel of the drive, refer to drawing HG 463009 G 001 at the back of this book.

- When the fan is replaced, ensure that the original wiring loom routing/fixing is preserved. This is an electrical safety requirement.

##### Replacing the Fan Start Capacitor

- Disconnect the capacitor wiring (two Faston connectors on the top of the capacitor).

- Remove the capacitor mounting nuts and replace with the new capacitor. Retighten the mounting nuts.

- Reconnect the capacitor wiring, taking care not to damage other components within the Inverter.

##### Replacing the Main Cooling Fan Only

- Remove the main fan housing.

- Disconnect the main cooling fan’s supply wiring loom at the terminal block on the bottom panel of the Inverter. Note the colour coding of the connections to the terminal block.

- Undo the fan mounting nuts. Remove the main cooling fan and fan start capacitor, taking care not to damage other components within drive. Replace with the new fan and fan start capacitor. Retighten the mounting nuts.

- Re-connect the fan wiring loom at the terminal block, ensuring that electrical safety isolation is preserved, refer to wiring diagram HJ 463151 D 001, Figure 8-7, page 8-11.

- Refit the lower panel assembly to the Inverter.

##### Replacing the Internal Extractor Fans

- Remove the main fan housing.

- Disconnect the main cooling fan’s supply wiring loom at the terminal block on the bottom panel of the Inverter. Note the colour coding of the connections to the terminal block.

- Undo the fan mounting nuts and remove the main cooling fan.

- While supporting the weight of the bottom panel assembly, remove the six M6 screws that secure it.

- Lower the bottom panel assembly out of the Inverter.

- Disconnect the supply cable to the faulty extractor fan.

- Replace the faulty fan and reconnect the supply to it.

- Re-fit the bottom panel assembly and tighten screws

- Re-fit the main cooling fan and secure in posiion.

- Reconnect the main cooling fan’s supply wiring loom at the terminal block on the bottom of the Inverter, refer to wiring diagram HJ 463151 D 001, Figure 8-7, page 8-11.

- Replace the main fan housing.

Figure 8-6  Wiring Diagram Fan Supply (Types 8 & 9)

Figure 8-7  Wiring Diagram Fan Supply (Type 10)

### Phase Assembly Replacement

The Inverter power stage consists of  3 identical phase assemblies. Each phase assembly consists of a heatsink, IGBT module, 1/3 of the input bridge, DC link capacitors and PCB ‘AH389193’.

We recommend that the whole phase assembly is carried as a spare part and replaced as a unit. Spare phase assemblies are available for Inverter Types 8, 9 & 10.

The spare phase assembly is supplied with a ‘service tray’ which is designed to assist in phase assembly replacement. It also protects the other delicate components within the Inverter during the replacement procedure.

- Observe all electrical warnings and static handling precautions.

###### Supplied Parts

- Service tray

- M5 x 10  hex head screws (2 off)

- Heatsink clamps (4 off). These are to be used in the replacement assembly if the original clamps are excessively distorted.

- Insulating caps (3 off)

###### Required Tools

- Square Drive ratchet wrench, 300mm extension, 8mm & 10mm socket

- No.3 Posidrive screwdriver

#### Phase Assembly Removal Procedure

- Undo the two, quarter-turn fasteners on the top of the Inverter casing and remove the front top cover (plastic). Repeat the operation on the bottom terminal cover.

- Disconnect the Operator Station 4-way cable from the P3 port on the Control PCB.

- Undo the four, quarter-turn fasteners to remove the Inverter’s front cover (metal). Take care not to damage PCBs beneath the cover when removing it.

- Remove the DC+ and DC- busbars at the top of the Inverter by undoing the two M6 captive nuts at the capacitor joining plate assembly, and the two M6 captive nuts at the external connection busbars. (Use the 300mm long extension  for this step).

- Remove the capacitor joining plate assembly by undoing the M6 captive washer nuts.
Note that the nuts on the left hand side of the M2 phase limb are covered with plastic insulating caps, (2 caps on Type 8, 3 caps on Types 9 & 10). These caps are a safety requirement and must be re-fitted.

- If you are removing the M3 phase limb from an Inverter which has a Brake unit fitted, you will have to remove the brake connecting plate. Refer to Chapter 3: “Installing the Inverter” - Inverter Brake Unit Installation Guidelines.

- Remove the two M6 captive nuts from the input busbar on the phase limb to be replaced. (Use the 300mm long extension for this step).

- Remove the two M6 hex bolts and washers from the output busbar on the phase limb to be replaced. (Use the 300mm long extension for this step).

- Disconnect the cable(s) from the printed circuit board on the phase limb to be replaced. Take note of PCB connectivity.

- Disconnect the earth bonding wire to the right of the phase limb to be replaced by removing the M4 captive nut at the chassis.

- Insert the `service tray’ underneath the phase limb to be removed and secure to the side panels of the Inverter using two M5 x 12 screws.

- Loosen the heatsink clamps (3 per phase assembly on Type 8, 4 per phase assembly on Types 9 & 10) and rotate through 90°.

- Carefully remove the phase limb assembly.

#### Phase Assembly Installation Procedure

- Replace any badly distorted heatsink clamps with the spare clamps provided.

- Carefully slide the replacement phase limb assembly into position, making sure that the studs on the input busbars (left-hand side) are located in the holes provided on the phase limb busbar. Re-fit nuts and washers, but do not tighten.

- Re-fit the output busbar bolts and washers and tighten to 6.8Nm torque.

- Secure the phase limb assembly to the chassis using the heatsink clamps.

- Remove the `service tray’.

- Tighten the input busbar nuts to 6.8Nm torque.

- Secure the earth bonding wire to the chassis and tighten to 4Nm torque.

- Reconnect the cable(s) to the phase limb assembly printed circuit board.

- Refit the capacitor joining plate, tightening the M6 captive nuts to 6.8Nm torque.

- Refit the plastic insulating caps to the (middle) M2 phase limb. They fit onto the left-hand side capacitor joining plate nuts, (2 caps on Type 8, 3 caps on Types 9 & 10). These caps are a safety requirement and must be re-fitted.

- Refit the DC+ and DC-  busbars, tightening the two M6 captive nuts on the capacitor joining plate and the two M6 captive nuts at the external connection busbars to 6.8Nm torque.

- Refit the brake connection plate and top cover if you have a Brake Unit fitted. Refer to Chapter 3: “Installing the Inverter” - Inverter Brake Unit Installation Guidelines.

- Replace the Inverter’s front cover (metal) which is attached using the four, quarter-turn fasteners (take care not to damage PCBs beneath the cover).

- Re-connect the Operator Station 4-way cable to the P3 port on the Control PCB.

- Re-fit the Inverter’s top cover (plastic) using the two quarter- turn fasteners.

- Re-fit the Inverter’s bottom terminal cover (plastic) using the two quarter- turn fasteners.